# Coastal Ridge Wind Farm — Weekly Maintenance Report

Reporting period: Week 37 | Prepared by: Maintenance Team

# 1. Fleet summary

Overall fleet availability was 96.2% this week, down from 98.1%. Two turbines required unscheduled attention.

# 2. WTG-3 — gearbox vibration

Abnormal gearbox vibration was detected on the high-speed shaft (4.7 mm/s RMS vs a 3.5 mm/s alarm threshold). The turbine was curtailed to 60% output. The maintenance team must inspect the WTG-3 gearbox with a borescope before returning it to normal operating conditions. Priority: high.

# 3. WTG-7 — cooling system alarm

The cooling system high-temperature alarm triggered twice overnight and coolant was 15% below minimum. This is a critical issue — the maintenance team must resolve the cooling system alarm and top up coolant immediately.

# 4. Other items

The monthly energy production report is due for management review. The WTG-1 nacelle anemometer shows a 3% calibration drift and should be recalibrated at the next service window. Gearbox filter spares are low and should be replenished.