Quarterly Management Brief

Coastal Ridge Renewable Operations — Q3 2026

# 1. Executive Overview

Coastal Ridge Renewable Operations delivered a solid Q3 2026 despite an unplanned mechanical outage late in the quarter. Fleet-wide availability averaged 97.1% across the quarter, against a target of 97.5%, with the shortfall concentrated in the final two weeks following the Turbine T-19 gearbox issue detailed below. Total energy delivered for the quarter was 54,600 MWh, 2.1% below forecast.

# 2. Financial Performance

Revenue for Q3 was $6.83M against a forecast of $6.95M, a 1.7% shortfall driven primarily by lost generation during the T-19 outage and the associated emergency maintenance spend. Operating expenses were $2.41M, $0.09M over budget due to the approved emergency capital expenditure for the gearbox replacement. Despite the shortfall, Q3 EBITDA margin held at 58.3%, within one point of target.

# 3. Operational KPIs

| KPI | Q3 Actual | Q3 Target | Q2 Actual |
| --- | --- | --- | --- |
| Fleet Availability | 97.1% | 97.5% | 98.4% |
| Energy Delivered (MWh) | 54,600 | 55,780 | 56,120 |
| Unplanned Downtime (hrs) | 412 | <300 | 180 |
| Safety Near-Misses Reported | 6 | n/a (leading indicator) | 3 |
| Lost-Time Injuries | 0 | 0 | 0 |

The rise in reported near-misses quarter-over-quarter (from 3 to 6) is viewed internally as a positive indicator of reporting culture rather than a deterioration in safety performance, particularly following the anchor-point near-miss discussed below — the site's philosophy is that under-reporting near-misses is the real risk, not the count itself.

# 4. Key Risks

## 4.1 Turbine T-19 Gearbox Failure — Financial Exposure

Turbine T-19 was taken offline on September 11, 2026 after condition monitoring detected sustained abnormal gearbox vibration, later confirmed by borescope inspection to be early-stage gear tooth pitting. The Q3 Operations Review approved an $85,000 gearbox replacement and expedited air-freight shipping at an additional $22,000, reducing the OEM's quoted lead time from 14 weeks to approximately 4 weeks. Re-commissioning is targeted for mid-October.

Estimated financial exposure: at current power purchase agreement rates, each week T-19 remains offline costs approximately $15,000 in lost generation revenue. Had the standard (non-expedited) shipping timeline been used, total exposure would have exceeded $210,000; the expedite decision is projected to hold total exposure to approximately $60,000 inclusive of the air-freight premium.

## 4.2 Spare-Parts Vendor Lead Time

The T-19 event exposed a structural risk in the site's spare-parts supply chain: the primary gearbox OEM's standard lead time of 14 weeks is not compatible with the financial impact of an extended single-turbine outage. Procurement is negotiating guaranteed expedite terms into the vendor contract renewal due in November.

## 4.3 Fall-Protection Anchor Points

A near-miss at Turbine T-22 on September 9, 2026, involving a loose internal fall-arrest anchor bolt, prompted an immediate site-wide policy change requiring a physical torque-check of anchor points before every climb (previously a visual check only), plus a full re-certification audit of all 36 turbines. No injury occurred, but this is flagged as a risk item pending confirmation that the audit, due September 25, 2026, is completed on schedule.

# 5. Q3 Achievements

Completed the annual blade inspection program across the full 36-turbine fleet two weeks ahead of schedule.

Zero lost-time injuries for the fifth consecutive quarter.

Onboarded two new electrical maintenance technicians, expanding in-house capacity ahead of Q4 planned works.

Resolved the T-19 gearbox issue detection-to-decision cycle in under one week, from first alarm to approved capital expenditure.

# 6. Strategic Priorities for Q4

Complete T-19 gearbox replacement and re-commissioning, targeting mid-October, and recover full fleet availability.

Close out the anchor-point re-certification audit and embed the revised torque-check procedure into standard onboarding.

Finalise the spare-parts vendor contract renewal with guaranteed expedite terms.

Present the Q4 budget proposal, incorporating the T-19 emergency spend against the maintenance contingency line.

# 7. Decision Required from Management

CRITICAL — While the immediate T-19 expedite decision has already been approved and actioned (see Section 4.1), management sign-off is still required on a related, longer-term item: Procurement has proposed pre-purchasing one spare gearbox unit to hold in site inventory, at a cost of $78,000, specifically to eliminate this class of lead-time exposure for any future gearbox failure across the fleet. Without this decision, the site remains exposed to the same 14-week standard lead time on any future occurrence. A decision is requested from the VP Operations by October 1, 2026 so the order can be placed within the OEM's current production run.

# 8. Budget Reallocation Summary

| Line Item | Q3 Budget | Q3 Actual | Variance |
| --- | --- | --- | --- |
| Routine Maintenance | $1.20M | $1.15M | -$0.05M |
| Emergency Maintenance (T-19) | $0.00M | $0.107M | +$0.107M |
| Safety & Compliance | $0.18M | $0.21M | +$0.03M |
| Training & Staffing | $0.25M | $0.24M | -$0.01M |

# 9. Closing Remarks

Q3 demonstrated the site's ability to detect and respond to a significant mechanical risk quickly, moving from first alarm to a funded, expedited resolution in under a week. The parallel safety process improvement following the T-22 near-miss shows the same discipline applied to leading safety indicators. Management's attention is requested on the Section 7 spare-inventory decision to reduce the site's exposure to a repeat of the T-19 scenario in future quarters.

Prepared by: M. Chen, VP Operations. Distribution: Executive Committee, Site Operations, Finance.